**PATLEC SERVICES - PORTABLE APPLIANCE TESTING ASSET REGISTER**

 **Client: Gavin Harris**

 **Reading 107 FM**

 **Radio House**

 **Madejski Stadium**

 **Reading RG2 0FN**

 **Test Date: 25 /08/12 Re-Test Date 25/08/13 Test Engineer: Colin Hyland**

|  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| **Asset No:** | **Item**  | **Class** | **Re****Test** | **Test Name** | **Reading** | **Pass****Fail** | **Room** | **Comment / Fuse** |
| 001MODELSERIAL | MonitorC02030202 | 1 | 12 | Earth (Cont) Ohm  Insulation MOhm Sub Leakage mAVisual Check  | 0.06>19.99<0.10Y | P | MAIN OFFICE | 13 AMP |
| 002MODELSERIAL | Kettle Lead | 1 | 12 | Earth Cont) Ohm  Insulation MOhmSub Leakage mAVisual Check  | 0.04>19.99N/AY | P | MAIN OFFICE | 13 AMP |
| 003MODELSERIAL | Kettle Lead | 1 | 12 | Earth (Cont) Ohm  Insulation MOhm Sub Leakage mAVisual Check  | 0.08>19.99N/AY | P | MAIN OFICE | 13 AMP |
| 004MODELSERIAL | 4 Way Lead | 2 | 12 | Earth (Cont) Ohm  Insulation MOhm Sub Leakage mAVisual Check  | 0.02>19.99N/AY | P | MAIN OFFICE | 13 AMP |
| 005MODELSERIAL | HP COMPUTER | 1 | 12 | Earth (Cont) Ohm Insulation MOhm Sub Leakage mAVisual Check  | 0.11>19.990.53Y | P | MAIN OFFICE |  |
| 006MODELSERIAL | HP PRINTER | 1 | 12 | Earth (Cont) Ohm Insulation MOhm Sub Leakage mAVisual Check  | 0.11>19.990.53Y | P | MAIN OFFICE |  |
| 007MODELSERIAL | KETTLE LEAD | 1 | 12 | Earth (Cont) Ohm Insulation MOhm Sub Leakage mAVisual Check  | 0.03>19.99N/AY | P | MAIN OFFICE | CHANGED PLUG13 AMP |
| 008MODELSERIAL | PRINTERKYOCERAFBC5025N | 1 | 12 | Earth (Cont) Ohm Insulation MOhm Sub Leakage mAVisual Check  | 0.05>19.990.33Y | P | MAIN OFFICE | 13 AMP |
| 009MODELSERIAL | TVGOODMANSPT29CA0923 | 2 | 12 | Earth (Cont) Ohm Insulation MOhm Sub Leakage mAVisual Check  | N/A>19.990.10Y | P | MAIN OFFICE | 5 AMP |
| 010MODELSERIAL | TVGOODMANSPT29CD1378 | 2 | 12 | Earth (Cont) Ohm Insulation MOhm Sub Leakage mAVisual Check  | N/A>19.990.10Y | P | MAIN OFFICE | 5 AMP |

**PATLEC SERVICES - PORTABLE APPLIANCE TESTING ASSET REGISTER**

 **Client: Gavin Harris**

 **Reading 107 FM**

 **Radio House**

 **Madejski Stadium**

 **Reading RG2 0FN**

 **Test Date: 25 /08/12 Re-Test Date 25/08/13 Test Engineer: Colin Hyland**

|  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| **Asset No:** | **Item**  | **Class** | **Re****Test** | **Test Name** | **Reading** | **Pass****Fail** | **Room** | **Comment / Fuse** |
| 0011MODELSERIAL | TV RECIEVER0682 | 2 | 12 | Earth (Cont) Ohm  Insulation MOhm Sub Leakage mAVisual Check  | N/A>19.99<0.10Y | P | MAIN OFFICE |  |
| 0012MODELSERIAL | KETLLE LEAD | 1 | 12 | Earth Cont) Ohm  Insulation MOhmSub Leakage mAVisual Check  | 0.06>19.99N/AY | P | MAIN OFFICE | 13 AMPCHANGED PLUG |
| 0013MODELSERIAL | KETTLE LEAD | 1 | 12 | Earth (Cont) Ohm  Insulation MOhm Sub Leakage mAVisual Check  | 0.04>19.99N/AY | P | MAIN OFICE | 13 AMPCHANGED PLUG |
| 0014MODELSERIAL | HP MONITORCNC54915BY | 2 | 12 | Earth (Cont) Ohm  Insulation MOhm Sub Leakage mAVisual Check  | N/A>19.990.60Y | P | MAIN OFFICE |  |
| 0015MODELSERIAL | HP COMPUTERCZC069OFXY | 1 | 12 | Earth (Cont) Ohm Insulation MOhm Sub Leakage mAVisual Check  | 0.07>19.990.50Y | P | MAIN OFFICE |  |
| 0016MODELSERIAL | SPEAKERSALTECA0940BS | 2 | 12 | Earth (Cont) Ohm Insulation MOhm Sub Leakage mAVisual Check  | N/A>19.990.10Y | P | MAIN OFFICE |  |
| 0017MODELSERIAL | 4 WAY EXTENSIONLEAD | 2 | 12 | Earth (Cont) Ohm Insulation MOhm Sub Leakage mAVisual Check  | 0.04>19.99N/AY | P | MAIN OFFICE | 13 AMP |
| 0018MODELSERIAL | 4 WAY EXTENSIONLEAD | 2 | 12 | Earth (Cont) Ohm Insulation MOhm Sub Leakage mAVisual Check  | 0.05>19.99N/AY | P | MAIN OFFICE | 13 AMP |
| 0019MODELSERIAL | KETTLE LEAD | 1 | 12 | Earth (Cont) Ohm Insulation MOhm Sub Leakage mAVisual Check  | 0.04>19.99N/AY | P | MAIN OFFICE | 13 AMP |
| 020MODELSERIAL | KETTLE LEAD | 1 | 12 | Earth (Cont) Ohm Insulation MOhm Sub Leakage mAVisual Check  | 0.06>19.99N/AY | P | MAIN OFFICE | 13 AMP |

**PATLEC SERVICES - PORTABLE APPLIANCE TESTING ASSET REGISTER**

 **Client: Gavin Harris**

 **Reading 107 FM**

 **Radio House**

 **Madejski Stadium**

 **Reading RG2 0FN**

 **Test Date: 25 /08/12 Re-Test Date 25/08/13 Test Engineer: Colin Hyland**

|  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| **Asset No:** | **Item**  | **Class** | **Re****Test** | **Test Name** | **Reading** | **Pass****Fail** | **Room** | **Comment / Fuse** |
| 0021MODELSERIAL | KETTLE LEAD | 1 | 12 | Earth (Cont) Ohm  Insulation MOhm Sub Leakage mAVisual Check  | 0.05>19.99N/AY | P | MAIN OFFICE | 13 AMP |
| 0022MODELSERIAL | KETLLE LEAD | 1 | 12 | Earth Cont) Ohm  Insulation MOhmSub Leakage mAVisual Check  | 0.03>19.99N/AY | P | MAIN OFFICE | 13 AMPCHANGED PLUG |
| 0023MODELSERIAL | HP MONITORCNN5521495 | 2 | 12 | Earth (Cont) Ohm  Insulation MOhm Sub Leakage mAVisual Check  | N/A>19.990.10Y | P | MAIN OFICE |  |
| 0024MODELSERIAL | HP MONITORCNN55241H1 | 2 | 12 | Earth (Cont) Ohm  Insulation MOhm Sub Leakage mAVisual Check  | N/A>19.990.10Y | P | MAIN OFFICE |  |
| 0025MODELSERIAL | KETLLE LEAD | 1 | 12 | Earth (Cont) Ohm Insulation MOhm Sub Leakage mAVisual Check  | 0.04>19.99N/AY | P | MAIN OFFICE | CHANGED PLUG 13 AMP |
| 0026MODELSERIAL | HP COMPUTER | 1 | 12 | Earth (Cont) Ohm Insulation MOhm Sub Leakage mAVisual Check  | 0.07>19.990.49Y | P | MAIN OFFICE |  |
| 0027MODELSERIAL | HP COMPUTER | 1 | 12 | Earth (Cont) Ohm Insulation MOhm Sub Leakage mAVisual Check  | 0.06>19.990.50Y | P | MAIN OFFICE |  |
| 0028MODELSERIAL | SPEAKERLABTEC | 1 | 12 | Earth (Cont) Ohm Insulation MOhm Sub Leakage mAVisual Check  | N/A>19.990.10Y | P | MAIN OFFICE | 3 AMP |
| 0029MODELSERIAL | MIXERDESICATE | 1 | 12 | Earth (Cont) Ohm Insulation MOhm Sub Leakage mAVisual Check  | 0.09>19.990.10Y | P | MAIN OFFICE |  |
| 030MODELSERIAL | ROUTER702134063 | 2 | 12 | Earth (Cont) Ohm Insulation MOhm Sub Leakage mAVisual Check  | N/A>19.990.10Y | P | MAIN OFFICE |  |

**PATLEC SERVICES - PORTABLE APPLIANCE TESTING ASSET REGISTER**

 **Client: Gavin Harris**

 **Reading 107 FM**

 **Radio House**

 **Madejski Stadium**

 **Reading RG2 0FN**

 **Test Date: 25 /08/12 Re-Test Date 25/08/13 Test Engineer: Colin Hyland**

|  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| **Asset No:** | **Item**  | **Class** | **Re****Test** | **Test Name** | **Reading** | **Pass****Fail** | **Room** | **Comment / Fuse** |
| 0031MODELSERIAL | KETTLE LEAD | 1 | 12 | Earth (Cont) Ohm  Insulation MOhm Sub Leakage mAVisual Check  | 0.01>19.99N/AY | P | MAIN OFFICE | 5 AMP |
| 0032MODELSERIAL | KETLLE LEAD | 1 | 12 | Earth Cont) Ohm  Insulation MOhmSub Leakage mAVisual Check  | 0.03>19.99N/AY | P | MAIN OFFICE | 5AMP |
| 0033MODELSERIAL | KETLLE LEAD | 1 | 12 | Earth (Cont) Ohm  Insulation MOhm Sub Leakage mAVisual Check  | 0.05>19.99N/AY | P | MAIN OFICE | 5AMP |
| 0034MODELSERIAL | KETLLE LEAD | 1 | 12 | Earth (Cont) Ohm  Insulation MOhm Sub Leakage mAVisual Check  | 0.04>19.99N/AY | P | MAIN OFFICE | 5AMP |
| 0035MODELSERIAL | KETLLE LEAD | 1 | 12 | Earth (Cont) Ohm Insulation MOhm Sub Leakage mAVisual Check  | 0.07>19.99N/AY | P | MAIN OFFICE | 5AMP |
| 0036MODELSERIAL | KETLLE LEAD | 1 | 12 | Earth (Cont) Ohm Insulation MOhm Sub Leakage mAVisual Check  | 0.04>19.99N/AY | P | MAIN OFFICE | 5AMP |
| 0037MODELSERIAL | KETLLE LEAD | 1 | 12 | Earth (Cont) Ohm Insulation MOhm Sub Leakage mAVisual Check  | 0.03>19.99N/AY | P | MAIN OFFICE | 5AMP |
| 0038MODELSERIAL | KETLLE LEAD | 1 | 12 | Earth (Cont) Ohm Insulation MOhm Sub Leakage mAVisual Check  | 0.03>19.99N/AY | P | MAIN OFFICE | 5AMP |
| 0039MODELSERIAL | KETLLE LEAD | 1 | 12 | Earth (Cont) Ohm Insulation MOhm Sub Leakage mAVisual Check  | 0.05>19.99N/AY | P | MAIN OFFICE | 5AMP |
| 040MODELSERIAL | KETLLE LEAD | 1 | 12 | Earth (Cont) Ohm Insulation MOhm Sub Leakage mAVisual Check  | 0.04>19.99N/AY | P | MAIN OFFICE | 5AMP |

**PATLEC SERVICES - PORTABLE APPLIANCE TESTING ASSET REGISTER**

 **Client: Gavin Harris**

 **Reading 107 FM**

 **Radio House**

 **Madejski Stadium**

 **Reading RG2 0FN**

 **Test Date: 25 /08/12 Re-Test Date 25/08/13 Test Engineer: Colin Hyland**

|  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| **Asset No:** | **Item**  | **Class** | **Re****Test** | **Test Name** | **Reading** | **Pass****Fail** | **Room** | **Comment / Fuse** |
| 0041MODELSERIAL | KETTLE LEAD | 1 | 12 | Earth (Cont) Ohm  Insulation MOhm Sub Leakage mAVisual Check  | 0.05>19.99N/AY | P | MAIN OFFICE | 5 AMP |
| 0042MODELSERIAL | 4 WAY EXTENSION LEAD | 2 | 12 | Earth Cont) Ohm  Insulation MOhmSub Leakage mAVisual Check  | 0.01>19.99N/AY | P | MAIN OFFICE | 13 AMP |
| 0043MODELSERIAL | 4 WAY EXTENSION LEAD | 2 | 12 | Earth (Cont) Ohm  Insulation MOhm Sub Leakage mAVisual Check  | 0.05>19.99N/AY | P | MAIN OFICE | 13 AMP |
| 0044MODELSERIAL | 4 WAY EXTENSION LEAD | 2 | 12 | Earth (Cont) Ohm  Insulation MOhm Sub Leakage mAVisual Check  | 0.03>19.99N/AY | P | MAIN OFFICE | 13 AMP |
| 0045MODELSERIAL | 4 WAY EXTENSION LEAD | 2 | 12 | Earth (Cont) Ohm Insulation MOhm Sub Leakage mAVisual Check  | 0.06>19.99N/AY | P | MAIN OFFICE | 13 AMP |
| 0046MODELSERIAL | HP MONITOR55240RS | 2 | 12 | Earth (Cont) Ohm Insulation MOhm Sub Leakage mAVisual Check  | N/A>19.990.50Y | P | MAIN OFFICE |  |
| 0047MODELSERIAL | HP MONITOR5511NPW | 2 | 12 | Earth (Cont) Ohm Insulation MOhm Sub Leakage mAVisual Check  | N/A>19.990.10Y | P | MAIN OFFICE |  |
| 0048MODELSERIAL | HP MONITOR55240RZ | 2 | 12 | Earth (Cont) Ohm Insulation MOhm Sub Leakage mAVisual Check  | N/A>19.990.49Y | P | MAIN OFFICE |  |
| 0049MODELSERIAL | HP MONITOR55241GJ | 2 | 12 | Earth (Cont) Ohm Insulation MOhm Sub Leakage mAVisual Check  | N/A>19.990.50Y | P | MAIN OFFICE |  |
| 050MODELSERIAL | KETTLE LEAD | 1 | 12 | Earth (Cont) Ohm Insulation MOhm Sub Leakage mAVisual Check  | 0.06>19.99N/AY | P | MAIN OFFICE | 5AMP |

**PATLEC SERVICES - PORTABLE APPLIANCE TESTING ASSET REGISTER**

 **Client: Gavin Harris**

 **Reading 107 FM**

 **Radio House**

 **Madejski Stadium**

 **Reading RG2 0FN**

 **Test Date: 25 /08/12 Re-Test Date 25/08/13 Test Engineer: Colin Hyland**

|  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| **Asset No:** | **Item**  | **Class** | **Re****Test** | **Test Name** | **Reading** | **Pass****Fail** | **Room** | **Comment / Fuse** |
| 0051MODELSERIAL | HP COMPUTER | 1 | 12 | Earth (Cont) Ohm  Insulation MOhm Sub Leakage mAVisual Check  | 0.07>19.990.49Y | P | MAIN OFFICE |  |
| 0052MODELSERIAL | HP COMPUTER | 1 | 12 | Earth Cont) Ohm  Insulation MOhmSub Leakage mAVisual Check  | 0.06>19.990.52Y | P | MAIN OFFICE |  |
| 0053MODELSERIAL | HP COMPUTER | 1 | 12 | Earth (Cont) Ohm  Insulation MOhm Sub Leakage mAVisual Check  | 0.04>19.990.50Y | P | MAIN OFICE |  |
| 0054MODELSERIAL | HP COMPUTER | 1 | 12 | Earth (Cont) Ohm  Insulation MOhm Sub Leakage mAVisual Check  | 0.04>19.990.49Y | P | MAIN OFFICE |  |
| 0055MODELSERIAL | SPEAKERSCREATIVE5BS260 | 2 | 12 | Earth (Cont) Ohm Insulation MOhm Sub Leakage mAVisual Check  | N/A>19.990.10Y | P | MAIN OFFICE |  |
| 0056MODELSERIAL | SPEAKERSLABTECH50189B | 2 | 12 | Earth (Cont) Ohm Insulation MOhm Sub Leakage mAVisual Check  | N/A>19.990.10Y | P | MAIN OFFICE | 3 AMP |
| 0057MODELSERIAL | SPEAKERSLOGITECH5-0156B | 2 | 12 | Earth (Cont) Ohm Insulation MOhm Sub Leakage mAVisual Check  | N/A>19.990.10Y | P | MAIN OFFICE |  |
| 0058MODELSERIAL | HP POWER ADAPTOR041224.00 | 2 | 12 | Earth (Cont) Ohm Insulation MOhm Sub Leakage mAVisual Check  | N/A>19.990.17Y | P | MAIN OFFICE |  |
| 0059MODELSERIAL | POWER SUPPLY | 2 | 12 | Earth (Cont) Ohm Insulation MOhm Sub Leakage mAVisual Check  | N/A>19.990.15Y | P | MAIN OFFICE |  |
| 060MODELSERIAL | LAMINATORLM120 | 2 | 12 | Earth (Cont) Ohm Insulation MOhm Sub Leakage mAVisual Check  | N/A>19.990.10Y | P | MAIN OFFICE | 3AMP |